## Test Plans
Self-cleansing flows Qsc (L/s) at minimum sewer slopes | [12 empty] | DN150 S v Qsc
| DN | Qsc (L/s) | Sminimum
| 150 | 3.8138 | 0.5%
| 225 | 6.4572 | 0.4%
| 300 | 17.0585 | 0.25%
ADWF QADWF (L/s) at minimum sewer slopes
- derived from Qsc, where Qsc is the PDWF, and from WSA 02-2014-3.1 Appendix C, where
| ADWF | 180 | L/s/EP
| PDWF | d *0.002083 * EP L/s | [10 empty] | DN225 S v Qsc
| where | d = 0.01(log10 EP)4 - 0.259(log10 EP)3 + 2.56(log10 EP)2 - 11.37log10 EP + 20.78
| DN | Sminimum | QPDWF (L/s) | EP | QADWF (L/s)
| 150 | 0.5% | 3.8138 | 418.7439 | 0.87238
| 225 | 0.4% | 6.4572 | 843.8278 | 1.758
| 300 | 0.25% | 17.0585 | 2945.0166 | 6.1355
Self-cleansing flows Qsc (L/s) v S
- derived by curve fitting from Sewer Pipe Sizing Calculator and resultantTable 1
| DN | A | B
S = A*QscB | 150 | 0.01047 | -0.57421
| 225 | 0.011537 | -0.57981 | [9 empty] | DN300 S v Qsc
| 300 | 0.012389 | -0.57749
Proportion of flow for tests | [6 empty] | Design flow Qd (L/s) at minimum sewer slopes
Base Type | Outlet | Inlet 90 | Inlet 180 | Inlet 270 | Riser |  | DN | Qd (L/s) | Sminimum
Type 180 | 100% |  | 100% |  |  |  | 150 | 10.9179 | 0.5%
Type 90 | 100% | 100% |  |  |  |  | 225 | 28.7902 | 0.4%
Type 90R | 100% | 100% |  |  | 20EP |  | 300 | 48.8341 | 0.25%
- Riser
Type 90/180 | 100% | 75% | 25% |  |  |  | Riser test inflows for 20EP
Type 90/180 | 100% | 50% | 50% |  |  |  | ADWF | 0.04 | L/s
Type 90/180R | 100% | 50% | 50% |  | 20EP |  | PDWF | 0.41 | L/s
|  | - Riser | - Riser |  |  |  | PWWF | 1.2 | L/s
Type 90/270 | 100% | 50% |  | 50% |  |  | see Sec 6.2 "High-level Inflow"
Testing Requirements
Select outlet DN in Table: "Qsc with minimum allowable slopes" (Cells shaded light orange)
The selected outlet DN will be copied to the other testing tables below.
The DN in laterals will be sized for the flow. Minimum slopes will be calculated from S = A*QscB (A & B from above)
Self-cleansing Requirements
Qsc with minimum allowable slopes
Base Type | Outlet |  |  | Inlet 90 |  |  | Inlet 180 |  |  | Inlet 270 |  |  | Riser
| DN | Qsc (L/s) | S | DN | Qsc (L/s) | S | DN | Qsc (L/s) | S | DN | Qsc (L/s) | S | QPDWF - 20EP (L/s)
Type 180 | 150 | 3.8138 | 0.5% |  |  |  | 150 | 3.8138 | 0.5%
Type 90 | 150 | 3.8138 | 0.5% | 150 | 3.8138 | 0.5%
Type 90R | 150 | 3.8138 | 0.5% | 150 | 3.4038 | 0.5182% | [6 empty] | 0.41
Type 90/180 | 300 | 17.0585 | 0.25% | 300 | 12.7939 | 0.2423% | 225 | 4.2646 | 0.4553%
Type 90/180 | 150 | 3.8138 | 0.5% | 150 | 1.9069 | 0.7227% | 150 | 1.9069 | 0.7227%
Type 90/180R | 150 | 3.8138 | 0.5% | 150 | 1.7019 | 0.7715% | 150 | 1.7019 | 0.7715% |  |  |  | 0.41
Type 90/270 | 150 | 3.8138 | 0.5% | 150 | 1.9069 | 0.7227% |  |  |  | 150 | 1.9069 | 0.7227%
QADWF with minimum allowable slopes, i.e., S as for Qsc
Base Type | Outlet |  |  | Inlet 90 |  |  | Inlet 180 |  |  | Inlet 270 |  |  | Riser
| DN | QADWF (L/s) | S | DN | QADWF (L/s) | S | DN | QADWF (L/s) | S | DN | QADWF (L/s) | S | QADWF - 20EP (L/s)
Type 180 | 150 | 0.87238 | 0.5% |  |  |  | 150 | 0.87238 | 0.5%
Type 90 | 150 | 0.87238 | 0.5% | 150 | 0.87238 | 0.5%
Type 90R | 150 | 0.87238 | 0.5% | 150 | 0.83238 | 0.5182% | [6 empty] | 0.04
Type 90/180 | 300 | 6.1355 | 0.25% | 300 | 4.6016 | 0.2423% | 225 | 1.5339 | 0.4553%
Type 90/180 | 150 | 0.87238 | 0.5% | 150 | 0.43619 | 0.7227% | 150 | 0.43619 | 0.7227%
Type 90/180R | 150 | 0.87238 | 0.5% | 150 | 0.41619 | 0.7715% | 150 | 0.41619 | 0.7715% |  |  |  | 0.04
Type 90/270 | 150 | 0.87238 | 0.5% | 150 | 0.43619 | 0.7227% |  |  |  | 150 | 0.43619 | 0.7227%
Hydraulic Requirements
Minimum slopes in & minimum slope out, i.e., S as for Qsc
Base Type | Outlet |  |  | Inlet 90 |  |  | Inlet 180 |  |  | Inlet 270 |  |  | Riser
| DN | Qd (L/s) | S | DN | Qd (L/s) | S | DN | Qd (L/s) | S | DN | Qd (L/s) | S | QPWWF - 20EP (L/s)
Type 180 | 150 | 10.9179 | 0.5% |  |  |  | 150 | 10.9179 | 0.5%
Type 90 | 150 | 10.9179 | 0.5% | 150 | 10.9179 | 0.5%
Type 90R | 150 | 10.9179 | 0.5% | 150 | 9.7179 | 0.5182% | [6 empty] | 1.2
Type 90/180 | 300 | 48.8341 | 0.25% | 300 | 36.6256 | 0.2423% | 225 | 12.2085 | 0.4553%
Type 90/180 | 150 | 10.9179 | 0.5% | 150 | 5.459 | 0.7227% | 150 | 5.459 | 0.7227%
Type 90/180R | 150 | 10.9179 | 0.5% | 150 | 4.859 | 0.7715% | 150 | 4.859 | 0.7715% |  |  |  | 1.2
Type 90/270 | 150 | 10.9179 | 0.5% | 150 | 5.459 | 0.7227% |  |  |  | 150 | 5.459 | 0.7227%
Supercritical 3% slope of lateral with greatest inflow
Minimum slopes for lessor inflow laterals & minimum slope out, i.e., S as for Qsc
Base Type | Outlet |  |  | Inlet 90 |  |  | Inlet 180 |  |  | Inlet 270 |  |  | Riser
| DN | Qd (L/s) | S | DN | Qd (L/s) | S | DN | Qd (L/s) | S | DN | Qd (L/s) | S | QPWWF - 20EP (L/s)
Type 180 | 150 | 10.9179 | 0.5% |  |  |  | 150 | 10.9179 | 3%
Type 90 | 150 | 10.9179 | 0.5% | 150 | 10.9179 | 3%
Type 90R | 150 | 10.9179 | 0.5% | 150 | 9.7179 | 3% | [6 empty] | 1.2
Type 90/180 | 300 | 48.8341 | 0.25% | 300 | 36.6256 | 0.7227% | 225 | 12.2085 | 3%
Type 90/180 | 150 | 10.9179 | 0.5% | 150 | 5.459 | 3% | 150 | 5.459 | 0.7227%
Type 90/180R | 150 | 10.9179 | 0.5% | 150 | 4.859 | 3% | 150 | 4.859 | 0.7715% |  |  |  | 1.2
Type 90/270 | 150 | 10.9179 | 0.5% | 150 | 5.459 | 3% |  |  |  | 150 | 5.459 | 0.7227%
Supercritical 7% slope of lateral with greatest inflow
Minimum slopes for lessor inflow laterals & minimum slope out, i.e., S as for Qsc
Base Type | Outlet |  |  | Inlet 90 |  |  | Inlet 180 |  |  | Inlet 270 |  |  | Riser
| DN | Qd (L/s) | S | DN | Qd (L/s) | S | DN | Qd (L/s) | S | DN | Qd (L/s) | S | QPWWF - 20EP (L/s)
Type 180 | 150 | 10.9179 | 0.5% |  |  |  | 150 | 10.9179 | 7%
Type 90 | 150 | 10.9179 | 0.5% | 150 | 10.9179 | 7%
Type 90R | 150 | 10.9179 | 0.5% | 150 | 9.7179 | 7% | [6 empty] | 1.2
Type 90/180 | 300 | 48.8341 | 0.25% | 300 | 36.6256 | 0.7227% | 225 | 12.2085 | 7%
Type 90/180 | 150 | 10.9179 | 0.5% | 150 | 5.459 | 7% | 150 | 5.459 | 0.7227%
Type 90/180R | 150 | 10.9179 | 0.5% | 150 | 4.859 | 7% | 150 | 4.859 | 0.7715% |  |  |  | 1.2
Type 90/270 | 150 | 10.9179 | 0.5% | 150 | 5.459 | 7% |  |  |  | 150 | 5.459 | 0.7227%